## Line
From Number | From Name | To Number | To Name | Circuit | Status | Branch Device Type | Xfrmr | R | X | B | Lim A MVA | Lim B MVA | Lim C MVA
1 | One | 2 | Two | 1 | Closed | Line | NO | 0 | 0.06 | 0.5 | 150 | 150 | 150
1 | One | 3 | Three | 1 | Closed | Line | NO | 0 | 0.24 | 0.05 | 150 | 150 | 150
2 | Two | 3 | Three | 1 | Closed | Line | NO | 0 | 0.18 | 0.04 | 120 | 120 | 120
2 | Two | 4 | Four | 1 | Closed | Line | NO | 0 | 0.18 | 0.04 | 100 | 100 | 100
2 | Two | 5 | Five | 1 | Closed | Line | NO | 0 | 0.12 | 0.03 | 200 | 100 | 100
3 | Three | 4 | Four | 1 | Closed | Line | NO | 0 | 0.03 | 0.02 | 222 | 100 | 100
4 | Four | 5 | Five | 1 | Closed | Line | NO | 0 | 0.24 | 0.05 | 60 | 100 | 100

## Load
Number of Bus | Name of Bus | Area Name of Load | Zone Name of Load | ID | Status | MW | Mvar | MVA | S MW | S Mvar
2 | Two | Top | 1 | 1 | Closed | 40 | 19.6 | 44.54 | 40 | 20
3 | Three | Top | 1 | 1 | Closed | 150 | 39.2 | 155.04 | 150 | 40
4 | Four | Top | 1 | 1 | Closed | 80 | 29.4 | 85.23 | 80 | 30
5 | Five | Top | 1 | 1 | Closed | 130 | 39.2 | 135.78 | 130 | 40

## Gen
Number of Bus | Name of Bus | ID | Status | Gen MW | Gen Mvar | Set Volt | AGC | AVR | Min MW | Max MW | Min Mvar | Max Mvar | Cost Model | Part. Factor
1 | One | 1 | Closed | 144.67 | 15.31 | 1.05 | YES | YES | 100 | 400 | -9900 | 9900 | Cubic | 1
2 | Two | 1 | Closed | 183.25 | 71.64 | 1.04 | YES | YES | 150 | 500 | -9900 | 9900 | Cubic | 1
4 | Four | 1 | Closed | 72.08 | 6.62 | 1 | YES | YES | 0 | 300 | -9900 | 9900 | Cubic | 1

## Bus
Number | Name | Area Name | Nom kV | PU Volt | Volt (kV) | Angle (Deg) | Load MW | Load Mvar | Gen MW | Gen Mvar | Switched Shunts Mvar | Act G Shunt MW | Act B Shunt Mvar | Area Num | Zone Num
1 | One | Top | 138 | 1.05 | 144.9 | 7.45 |  |  | 144.67 | 15.31 |  | 0 | 0 | 1 | 1
2 | Two | Top | 138 | 1.04 | 143.52 | 4.89 | 40 | 19.6 | 183.25 | 71.64 |  | 0 | 0 | 1 | 1
3 | Three | Top | 138 | 1.0004 | 138.056 | -0.87 | 150 | 39.2 |  |  |  | 0 | 0 | 1 | 1
4 | Four | Top | 138 | 1 | 138 | -0.38 | 80 | 29.4 | 72.08 | 6.62 |  | 0 | 0 | 1 | 1
5 | Five | Top | 138 | 0.99191 | 136.883 | -2.68 | 130 | 39.2 |  |  |  | 0 | 0 | 1 | 1

## YBus
Number | Name | Bus 1 | Bus 2 | Bus 3 | Bus 4 | Bus 5
1 | One | 0.00 - j20.56 | -0.00 + j16.67 | -0.00 + j4.17
2 | Two | -0.00 + j16.67 | 0.00 - j35.81 | -0.00 + j5.56 | -0.00 + j5.56 | -0.00 + j8.33
3 | Three | -0.00 + j4.17 | -0.00 + j5.56 | 0.00 - j43.00 | -0.00 + j33.33
4 | Four |  | -0.00 + j5.56 | -0.00 + j33.33 | 0.00 - j43.00 | -0.00 + j4.17
5 | Five |  | -0.00 + j8.33 |  | -0.00 + j4.17 | 0.00 - j12.46